| MIFAB, Inc. | July 2008 |
| --- | --- |
| 1321 West 119th Street |  |
| Chicago, IL 60643-5109 |  |
| Toll Free (800) 465-2736 |  |
| Phone (773) 341-3030 | E-Mail mail@mifab.com |
| Fax (773) 341-3049 | Web Site www.mifab.com |

Product Guide Specification

Specifier Notes: This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format. The section must be carefully reviewed and edited by the Architect to meet the requirements of the project and local building code. Coordinate this section with other specification sections and the drawings. Delete all “Specifier Notes” when editing this section.

SECTION 22150

FLOOR DRAINS

Specifier Notes: This section covers MIFAB “F1320C” floor drain with 9-inch round adjustable tractor grate. Consult MIFAB for assistance in editing this section for the specific application.

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	Floor drains with 9-inch round adjustable tractor grate.

1.2	RELATED SECTIONS

Specifier Notes: Edit the following list of related sections as required for the project. List other sections with work directly related to this section.

A.	Section 22100 - Building Services Piping.

B.	Section 22400 - Plumbing Fixtures and Equipment.

1.3	REFERENCES

A.	ASME A112.6.3 - Floor and Trench Drains.

B.	ASTM A 48 - Standard Specification for Gray Iron Castings.

1.4	SUBMITTALS

A.	Comply with Section 01330 - Submittal Procedures.

B.	Product Data:  Submit manufacturer's product data, including installation instructions.

1.5	DELIVERY, STORAGE, AND HANDLING

A.	Delivery:  Deliver materials to site in manufacturer's original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

B.	Storage:  Store materials in clean, dry area indoors in accordance with manufacturer's instructions.

C.	Handling:  Protect materials and finish from damage during handling and installation.

PART 2	PRODUCTS

2.1	MANUFACTURER

Specifier Notes: Specify MIFAB, Inc. in the US or MIFAB Canada in Canada

A.	[MIFAB, Inc., 1321 West 119th Street, Chicago, IL. 60643-5109  Toll Free (800) 465-2736.]

Web Site www.mifab.com  E-Mail mail@mifab.com.

2.2	MATERIALS

A.	Floor Drains:  F1320C floor drain with 9-inch round adjustable tractor grate.

1.	Compliance:  ASME A112.6.3.

2.	Load Rating:  Special-duty load class, over 10,000 pounds.

3.	Body:  A1, 8-inch (200-mm) diameter body.  Lacquered, ASTM A 48, Class 25 cast iron body with anchor flange and weepholes.  4-inch (100-mm) throat.  4-inch (100-mm) NPS machined integral body threads.

4.	Tractor Grate:  1-inch (25-mm) thick, 9-inch (230-mm) diameter, adjustable, ductile iron tractor grate.  3/8-inch (9-mm) maximum width drainage slots.

Specifier Notes: Specify pipe size.

5.	Pipe Size:  [2 inches (50 mm)]  [3 inches (75 mm)]  [4 inches (100 mm)]  [6 inches (150 mm)].

6.	Membrane Clamp:  ASTM A 48, Class 25 cast iron membrane clamp ring with primary and secondary weepholes for waterproofing membrane.

Specifier Notes: Specify required floor drain options and revise above text as necessary. Delete options not required. Consult MIFAB for additional information.

B.	Floor Drain Options:

1.	Grate Veneer:  [Nickel bronze]  [Type 304 stainless steel with No. 4 satin finish].

2.	3M epoxy finish.

3.	Sediment bucket.

4.	Vandal proof.

5.	Trap seal primer tapping.

6.	Backwater valve.

7.	Acid-resistant epoxy coating.

8.	Galvanized top assembly.

9.	All galvanized.

10.	Non-tilt grate.

11.	Extension.

12.	Square top.

13.	Dome grate.

14.	Body:  [Bronze]  [Type 304 stainless steel]  [Type 316 stainless steel].

15.	Socket Connection Body:  [PVC]  [ABS].

16.	Closure plug.

17.	Deck clamp.

18.	Sump receiver.

19.	Lacquered cast iron funnels.

20.	Threaded side outlet.

21.	Client logo.

22.	Funnel:  [4-inch round]  [6-inch round]  [4-inch by 9-inch oval]  [6-inch by 3-inch by 1-inch].

23.	Outlet:  [Push-on]  [Threaded]  [Inside caulk].

24.	Non-adjustable top.

25.	Elastomeric flange.

PART 3	EXECUTION

3.1	EXAMINATION

A.	Examine areas to receive floor drains.  Notify Architect of conditions that would adversely affect installation or subsequent use.  Do not proceed with installation until unsatisfactory conditions are corrected.

3.2	INSTALLATION

A.	Install floor drains in accordance with manufacturer's instructions at locations indicated on the drawings.

B.	Install floor drains plumb, level, and to correct elevation.

C.	Ensure top of floor drains are flush with top of finished floor.

D.	Install floor drains using manufacturer's supplied hardware.

3.3	PROTECTION

A.	Protect installed floor drains from damage during construction.

END OF SECTION